JOB HAZARD ANALYSIS (JHA)
Lighting installation · Electrical · Template from SiteSorted
1. BUSINESS AND JOB DETAILS
	Company
	

	Business address and phone
	

	Job / scope of work
	

	Site address
	

	Client / general contractor
	

	Start date and duration
	

	Working hours
	

	Supervisor
	

	Prepared by
	

	Document number and revision
	

	Competent person
	

	Review date
	


2. JOB STEPS, HAZARDS AND CONTROLS
	#
	Job step
	Hazards
	Risk before
	Controls
	Risk after
	Responsible

	1
	Isolate the lighting circuit, apply lockout/tagout and test to prove dead
	Electric shock from live wiring
	Critical
	- Isolate the power before any work. Do not work live. [Elimination]
- Lock out and tag the disconnecting means with your own personal lock and tag so the circuit cannot be energized (29 CFR 1926.417). [Engineering (guarding)]
- Test before you touch: prove dead at the point of work with a tested voltage tester. [Engineering]
- Only qualified persons work on or near exposed energized parts. [Administrative]
- Check for back feeds from solar, batteries and generators that can keep a circuit live after the main switch is off. [Administrative]
- If energized work cannot be avoided, use an energized work permit, a safety observer and insulated tools, following NFPA 70E. [Administrative]
- Wear insulated gloves, arc-rated clothing and a face shield when testing or working near live parts. [PPE]
	Medium
	

	2
	Set up a platform ladder or aerial lift on level ground under the work
	Falling from a ladder
Falling from height
Aerial lift tip-over or crush
	Critical
	- Use a platform ladder, mobile scaffold or aerial lift for longer jobs instead of a straight ladder. [Substitution]
- Use Type I, IA or IAA ladders in good condition. Tag and remove any damaged ladder. [Engineering]
- Set extension ladders at a 4 to 1 angle on firm, level ground, secured, and reaching 3 feet above the landing. [Engineering]
- Use ladders only for short, light work. Do not carry heavy or awkward loads up a ladder. [Administrative]
- Keep three points of contact and your belt buckle between the stiles. Do not overreach. [Administrative]
- Do the work from the ground where you can, for example pre-assemble on the ground or use extension poles. [Elimination]
- Install guardrails or edge protection on all open edges before work starts. [Engineering (guarding)]
- Use a scaffold, mobile work platform or aerial lift instead of working off a ladder. [Engineering]
- Where edge protection is not practical, use a fall restraint or fall arrest system on a rated anchor point. [Engineering]
- Provide fall protection at 6 feet or more and train workers to recognize fall hazards (29 CFR 1926.503). [Administrative]
- Have a rescue plan so a worker hanging in a harness can be brought down within minutes. [Administrative]
- Check the ground before setting up. Use outriggers and spreader pads, and keep clear of trenches, pits and slopes. [Engineering]
- Use a platform with tilt alarm and secondary guarding (anti-entrapment) where there is an overhead crush risk. [Engineering]
- Only trained and authorized operators use aerial lifts and scissor lifts (29 CFR 1926.453 for boom lifts, 1926.452(w) and 1926.454 for scissor lifts). [Administrative]
- Do a pre-start check each day. Keep a trained person on the ground who can lower the platform in an emergency. [Administrative]
- Never exceed the safe working load, climb on the rails or use a ladder in the basket. [Administrative]
- In boom-type platforms, wear a harness clipped to the basket anchor point. [PPE]
	Medium
	

	3
	Cut holes for downlights, wearing glasses and a dust mask and checking for insulation and cables
	General dust
Eye injuries
Falling through a floor opening or void
	Critical
	- Use low-dust products, such as dust-reduced or pre-mixed compounds. [Substitution]
- Seal off the work area with plastic sheeting in occupied buildings. [Engineering (guarding)]
- Use tools with dust extraction and a vacuum for clean up. [Engineering]
- Lightly mist the area with water to keep dust down, away from anything electrical. [Engineering]
- Never dry sweep or blow dust off with compressed air. [Administrative]
- Use tool guards and screens to stop flying particles. [Engineering]
- Use dust extraction and water to keep dust out of the air. [Engineering]
- Keep others out of the area when cutting, grinding or chipping. [Administrative]
- Keep an eye wash station or eye wash bottles on site. [Administrative]
- Wear safety glasses at all times, goggles for dust and chemicals, and a face shield for grinding. [PPE]
- Cover every hole with a secured cover marked "HOLE" or "COVER" that can hold twice the weight it may carry. [Engineering (guarding)]
- Put guardrails with toe boards around stairwells, elevator shafts, floor holes and open edges. [Engineering (guarding)]
- Install stairs early and fit temporary handrails as soon as they go in. [Engineering]
- Never remove a cover or guardrail without approval. Put it back straight away. [Administrative]
- Inspect covers and barriers daily and after other trades have been through. [Administrative]
	Medium
	

	4
	Mount fittings, keeping clearance from insulation and timber
	Fire from hot works
Repetitive work and awkward postures
	Critical
	- Use cold work methods where you can, such as bolting, press fittings or cutting with a saw instead of a torch. [Elimination]
- Move anything that can burn at least 35 feet away, or cover it with fire blankets. [Engineering (guarding)]
- Use fire-resistant screens to stop sparks reaching people or gaps in walls and floors. [Engineering]
- Get a hot work permit before starting. [Administrative]
- Keep a charged fire extinguisher and fire blanket at the work spot. [Administrative]
- Keep a fire watch during the work and for at least 60 minutes after you finish (NFPA 51B), longer if the permit says so. [Administrative]
- Check for smoldering behind walls, in ceilings and under floors before you leave. [Administrative]
- Wear flame-resistant clothing, welding gloves and eye or face protection. [PPE]
- Use tools that cut the effort: powered screwdrivers, long-handled tools and extension poles for overhead work. [Substitution]
- Set work up at waist height on benches or trestles where you can. [Engineering]
- Use light tools with good grips, and keep blades and bits sharp. [Engineering]
- Rotate tasks and take short breaks every hour on repetitive work. [Administrative]
- Warm up before heavy physical work and report aches and pains early. [Administrative]
- Wear knee pads for kneeling work and gloves for grip. [PPE]
	Medium
	

	5
	Test, restore power and clean up
	Electric shock from live wiring
Poor housekeeping and waste
	Critical
	- Electric shock from live wiring: see step 1 for the full controls [Administrative]
- Order materials to size and send packaging back where you can. [Elimination]
- Put dumpsters and waste chutes close to the work. [Engineering]
- Clean as you go, and do a full clean up at the end of each day. [Administrative]
- Keep exits, stairs and walkways clear at all times. [Administrative]
- Stack materials neatly on level ground, away from edges. [Administrative]
- Wear gloves when handling waste. [PPE]
	Medium
	


3. PPE, PLANT AND PERMITS
	Required PPE
	Plant and equipment (licence or training)
	Permits and plans

	Safety-toe boots (ASTM F2413)
Safety glasses (ANSI Z87.1)
Work gloves
N95 respirator
Rubber insulating gloves
Arc flash PPE (NFPA 70E)
Hard hat (ANSI Z89.1)
Personal fall arrest system (harness)
High-visibility safety apparel, ANSI/ISEA 107 Class 2 or 3 (Type R near roadways)
Safety goggles (ANSI Z87.1)
Face shield (ANSI Z87.1)
Welding gloves
Coveralls
Knee pads
	Electrical test meter
Platform ladder
Power drill
Hand tools
Scissor lift (Trained operator: OSHA treats scissor lifts as mobile scaffolds (29 CFR 1926.452(w), 1926.454); ANSI A92.24 training and familiarization)
	Lockout/tagout (1926.417)
Written fall protection plan (only where guardrails, nets or personal fall arrest are not feasible, 1926.502(k))
Hot work permit (fire watch at least 60 minutes after, NFPA 51B)


4. EMERGENCY ARRANGEMENTS
	Emergency number: 911
	

	Nearest hospital
	

	Assembly point
	

	First aid / CPR person
	

	First aid kit location
	

	Fire extinguisher location
	


5. MONITORING, REVIEW AND LEGAL BASIS
The supervisor checks the controls at the start of each day and during the work. Stop work and review this document if the job, the crew or the site conditions change, or after any incident or near miss.
Legal basis: OSH Act Section 5(a)(1) and 29 CFR 1926, Safety and Health Regulations for Construction (incl. 1926.20 and 1926.21).
Keep this JHA on site during the job, and keep it with the training and inspection records for at least 1 year after the job (longer if your state plan or general contractor requires it). OSHA does not set a retention period for JHAs themselves.
6. SIGN-OFF
By signing below, each person confirms they have read and understood this JHA and will follow it.
	Name
	Role
	Tickets / licences
	Signature
	Date

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


Free template from SiteSorted. Make it in 2 minutes and get it signed on your phone: https://sitesorted.pages.dev/us/jha/electrical/lighting-installation/
